## levels_and_zones
level | equipments | zones | source_url
Plantroom | default | Plantroom, All | default
Level B1 | SAF-B-1, SAF-B-2, SAF-B-3, SAF-G-1, TEF-15-2, CPEF, GREF-15-1, Bakery AC Unit | Plantroom, All, B-1, B-2, B-3, G-1 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005018
Ground | PAC-G, PAC-G-01, PAC-G-02, PAC-G-03, PAC-G-04, OAF-G-01 | Plantroom, All, G, G-01, G-02, G-03, G-04 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005017
Level 1 | VAV-1-E-1, VAV-1-E-2, VAV-1-C-1, VAV-1-C-2, VAV-1-C-3, VAV-1-C-4, VAV-1-N-1, VAV-1-N-2, AHU-E-1, AHU-C-1, AHU-N-1 | Plantroom, All, 1-E-1, 1-E-2, 1-C-1, 1-C-2, 1-C-3, 1-C-4, 1-N-1, 1-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005001
Level 2 | VAV-2-E-1, VAV-2-E-2, VAV-2-C-1, VAV-2-C-2, VAV-2-C-3, VAV-2-C-4, VAV-2-N-1, VAV-2-N-2, AHU-E-2, AHU-C-2, AHU-N-2 | Plantroom, All, 2-E-1, 2-E-2, 2-C-1, 2-C-2, 2-C-3, 2-C-4, 2-N-1, 2-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005002
Level 3 | VAV-3-E-1, VAV-3-E-2, VAV-3-C-1, VAV-3-C-2, VAV-3-C-3, VAV-3-C-4, VAV-3-N-1, VAV-3-N-2, AHU-E-3, AHU-C-3, AHU-N-3 | Plantroom, All, 3-E-1, 3-E-2, 3-C-1, 3-C-2, 3-C-3, 3-C-4, 3-N-1, 3-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005003
Level 4 | VAV-4-E-1, VAV-4-E-2, VAV-4-C-1, VAV-4-C-2, VAV-4-C-3, VAV-4-C-4, VAV-4-N-1, VAV-4-N-2, AHU-E-4, AHU-C-4, AHU-N-4 | Plantroom, All, 4-E-1, 4-E-2, 4-C-1, 4-C-2, 4-C-3, 4-C-4, 4-N-1, 4-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005004
Level 5 | VAV-5-E-1, VAV-5-E-2, VAV-5-C-1, VAV-5-C-2, VAV-5-C-3, VAV-5-C-4, VAV-5-N-1, VAV-5-N-2, AHU-E-5, AHU-C-5, AHU-N-5 | Plantroom, All, 5-E-1, 5-E-2, 5-C-1, 5-C-2, 5-C-3, 5-C-4, 5-N-1, 5-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005005
Level 6 | VAV-6-E-1, VAV-6-E-2, VAV-6-C-1, VAV-6-C-2, VAV-6-C-3, VAV-6-C-4, VAV-6-N-1, VAV-6-N-2, AHU-E-6, AHU-C-6, AHU-N-6 | Plantroom, All, 6-E-1, 6-E-2, 6-C-1, 6-C-2, 6-C-3, 6-C-4, 6-N-1, 6-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005006
Level 7 | VAV-7-E-1, VAV-7-E-2, VAV-7-C-1, VAV-7-C-2, VAV-7-C-3, VAV-7-C-4, VAV-7-N-1, VAV-7-N-2, AHU-E-7, AHU-C-7, AHU-N-7 | Plantroom, All, 7-E-1, 7-E-2, 7-C-1, 7-C-2, 7-C-3, 7-C-4, 7-N-1, 7-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005007
Level 8 | VAV-8-E-1, VAV-8-E-2, VAV-8-C-1, VAV-8-C-2, VAV-8-C-3, VAV-8-C-4, VAV-8-N-1, VAV-8-N-2, AHU-E-8, AHU-C-8, AHU-N-8 | Plantroom, All, 8-E-1, 8-E-2, 8-C-1, 8-C-2, 8-C-3, 8-C-4, 8-N-1, 8-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005008
Level 9 | VAV-9-E-1, VAV-9-E-2, VAV-9-C-1, VAV-9-C-2, VAV-9-C-3, VAV-9-C-4, VAV-9-N-1, VAV-9-N-2, AHU-E-9, AHU-C-9, AHU-N-9 | Plantroom, All, 9-E-1, 9-E-2, 9-C-1, 9-C-2, 9-C-3, 9-C-4, 9-N-1, 9-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005009
Level 10 | VAV-10-E-1, VAV-10-E-2, VAV-10-C-1, VAV-10-C-2, VAV-10-C-3, VAV-10-C-4, VAV-10-N-1, VAV-10-N-2, AHU-E-10, AHU-C-10, AHU-N-10 | Plantroom, All, 10-E-1, 10-E-2, 10-C-1, 10-C-2, 10-C-3, 10-C-4, 10-N-1, 10-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005010
Level 11 | VAV-11-E-1, VAV-11-E-2, VAV-11-C-1, VAV-11-C-2, VAV-11-C-3, VAV-11-C-4, VAV-11-N-1, VAV-11-N-2, AHU-E-11, AHU-C-11, AHU-N-11 | Plantroom, All, 11-E-1, 11-E-2, 11-C-1, 11-C-2, 11-C-3, 11-C-4, 11-N-1, 11-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005011
Level 12 | VAV-12-E-1, VAV-12-E-2, VAV-12-C-1, VAV-12-C-2, VAV-12-C-3, VAV-12-C-4, VAV-12-N-1, VAV-12-N-2, AHU-E-12, AHU-C-12, AHU-N-12 | Plantroom, All, 12-E-1, 12-E-2, 12-C-1, 12-C-2, 12-C-3, 12-C-4, 12-N-1, 12-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005012
Level 13 | VAV-13-E-1, VAV-13-E-2, VAV-13-C-1, VAV-13-C-2, VAV-13-C-3, VAV-13-C-4, VAV-13-N-1, VAV-13-N-2, AHU-E-13, AHU-C-13, AHU-N-13 | Plantroom, All, 13-E-1, 13-E-2, 13-C-1, 13-C-2, 13-C-3, 13-C-4, 13-N-1, 13-N-2 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005013
Level 14 | AHU-N1-14, AHU-N2-14, AHU-C-14, AHU-E-14 | Plantroom, All, N1-14, N2-14, C-14, E-14 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005014
Level 15 | TPCWP-1, TPCWP-2, TSCWP-1, TSCWP-2, CHWP-1, CHWP-2, CWP-1, CWP-2, Chiller-1, Chiller-2, TGEF-15-1, TEF-15-1, TEF-15-2, GREF-15-1, AHU-E-14, AHU-C-14, AHU-N2-14 | Plantroom, All | http://103.21.132.234/page?dds=ADVCONTR/99E/00005015
Roof | Cooling Tower-1, Cooling Tower-2, Boiler-1, Boiler-2, Boiler-3, HWP-1, HWP-2, HWP-3, PAC-16, TEF-16-1 | Plantroom, All | http://103.21.132.234/page?dds=ADVCONTR/99E/00005016

## equipment_list
equipment_name | level_select | zone_select | equipment_type_select | device_id | source_url
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005001
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005001
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005001
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005002
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005002
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005002
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005003
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005003
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005003
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005004
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005004
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005004
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005005
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005005
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005005
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005006
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005006
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005006
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005007
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005007
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005007
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005008
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005008
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005008
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005009
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005009
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005009
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005010
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005010
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005010
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005011
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005011
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005011
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005012
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005012
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005012
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005013
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005013
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005013
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005014
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005014
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005014
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | http://103.21.132.234/page?dds=ADVCONTR/99E/00005014
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001005
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001002
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001006
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001003
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001007
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001004
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001008
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001009
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001013
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001014
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001011
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | http://103.21.132.234/page?dds=ADVCONTR/99E/00001012
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | http://103.21.132.234/page?dds=ADVCONTR/99E/DeviceTemplates/00000999&device=415035
SAF-B-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002019
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002022
SAF-B-3 | Level B1 | Plantroom | Supply Air Fan | 100004 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002020
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002021
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002016
TEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002011
TEF-15-2 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002012
GREF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002013
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002018
KEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002015
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002017
TEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | http://103.21.132.234/page?dds=ADVCONTR/99E/00002014
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | http://103.21.132.234/page?dds=ADVCONTR/99E/DeviceTemplates/00000999&device=205004
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | http://103.21.132.234/page?dds=ADVCONTR/99E/DeviceTemplates/00000999&device=205004
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | http://103.21.132.234/page?dds=ADVCONTR/99E/DeviceTemplates/00000999&device=205004
TEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans |  | http://103.21.132.234/page?dds=ADVCONTR/99E/00002010

## points_list
equipment_name | level_select | zone_select | equipment_type_select | device_id_select | graphic_point_name | graphic_value | graphic_unit | underlying_point_name
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Min OA Position |  | % | Analog Value 85
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Time Schedule |  |  | Binary Value 40
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | After Hours (old) |  |  | Binary Value 51
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | After Hours (new) |  |  | Binary Value 43
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Filter Status |  |  | Binary Value 44
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Fan Call |  |  | Binary Output 0
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Fan Status |  |  | Binary Value 34
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Fan Fault |  |  | Binary Value 35
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Multiplier SP |  | % | Analog Value 67
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | SA Temp SP |  | °C | Analog Value 13
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | SA Temperature |  | °C | Analog Value 0
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | RA Temperature |  | °C | Analog Value 1
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Economy Cycle |  |  | Binary Value 30
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | Fan Speed |  | % | Analog Output 2
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-1 | Level 1 | Plantroom | Air Handling Units | 101006 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Min OA Position |  | % | Analog Value 85
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Time Schedule |  |  | Binary Value 40
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | After Hours (old) |  |  | Binary Value 51
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | After Hours (new) |  |  | Binary Value 43
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Filter Status |  |  | Binary Value 44
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Fan Call |  |  | Binary Output 0
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Fan Status |  |  | Binary Value 34
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Fan Fault |  |  | Binary Value 35
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Multiplier SP |  | % | Analog Value 67
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | SA Temp SP |  | °C | Analog Value 13
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | SA Temperature |  | °C | Analog Value 0
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | RA Temperature |  | °C | Analog Value 1
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Economy Cycle |  |  | Binary Value 30
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | Fan Speed |  | % | Analog Output 2
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-1 | Level 1 | Plantroom | Air Handling Units | 101005 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Min OA Position |  | % | Analog Value 85
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Time Schedule |  |  | Binary Value 40
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | After Hours (old) |  |  | Binary Value 51
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | After Hours (new) |  |  | Binary Value 43
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Filter Status |  |  | Binary Value 44
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Fan Call |  |  | Binary Output 0
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Fan Status |  |  | Binary Value 34
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Fan Fault |  |  | Binary Value 35
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Multiplier SP |  | % | Analog Value 67
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | SA Temp SP |  | °C | Analog Value 13
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | SA Temperature |  | °C | Analog Value 0
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | RA Temperature |  | °C | Analog Value 1
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Economy Cycle |  |  | Binary Value 30
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | Fan Speed |  | % | Analog Output 2
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-1 | Level 1 | Plantroom | Air Handling Units | 101007 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Min OA Position |  | % | Analog Value 85
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Time Schedule |  |  | Binary Value 40
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | After Hours (old) |  |  | Binary Value 51
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | After Hours (new) |  |  | Binary Value 43
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Filter Status |  |  | Binary Value 44
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Fan Call |  |  | Binary Output 0
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Fan Status |  |  | Binary Value 34
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Fan Fault |  |  | Binary Value 35
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Multiplier SP |  | % | Analog Value 67
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | SA Temp SP |  | °C | Analog Value 13
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | SA Temperature |  | °C | Analog Value 0
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | RA Temperature |  | °C | Analog Value 1
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Economy Cycle |  |  | Binary Value 30
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | Fan Speed |  | % | Analog Output 2
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-2 | Level 2 | Plantroom | Air Handling Units | 102026 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Min OA Position |  | % | Analog Value 85
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Time Schedule |  |  | Binary Value 40
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | After Hours (old) |  |  | Binary Value 51
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | After Hours (new) |  |  | Binary Value 43
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Filter Status |  |  | Binary Value 44
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Fan Call |  |  | Binary Output 0
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Fan Status |  |  | Binary Value 34
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Fan Fault |  |  | Binary Value 35
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Multiplier SP |  | % | Analog Value 67
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | SA Temp SP |  | °C | Analog Value 13
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | SA Temperature |  | °C | Analog Value 0
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | RA Temperature |  | °C | Analog Value 1
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Economy Cycle |  |  | Binary Value 30
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | Fan Speed |  | % | Analog Output 2
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-2 | Level 2 | Plantroom | Air Handling Units | 102025 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Min OA Position |  | % | Analog Value 85
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Time Schedule |  |  | Binary Value 40
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | After Hours (old) |  |  | Binary Value 51
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | After Hours (new) |  |  | Binary Value 43
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Filter Status |  |  | Binary Value 44
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Fan Call |  |  | Binary Output 0
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Fan Status |  |  | Binary Value 34
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Fan Fault |  |  | Binary Value 35
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Multiplier SP |  | % | Analog Value 67
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | SA Temp SP |  | °C | Analog Value 13
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | SA Temperature |  | °C | Analog Value 0
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | RA Temperature |  | °C | Analog Value 1
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Economy Cycle |  |  | Binary Value 30
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | Fan Speed |  | % | Analog Output 2
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-2 | Level 2 | Plantroom | Air Handling Units | 102027 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Min OA Position |  | % | Analog Value 85
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Time Schedule |  |  | Binary Value 40
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | After Hours (old) |  |  | Binary Value 51
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | After Hours (new) |  |  | Binary Value 43
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Filter Status |  |  | Binary Value 44
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Fan Call |  |  | Binary Output 0
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Fan Status |  |  | Binary Value 34
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Fan Fault |  |  | Binary Value 35
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Multiplier SP |  | % | Analog Value 67
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | SA Temp SP |  | °C | Analog Value 13
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | SA Temperature |  | °C | Analog Value 0
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | RA Temperature |  | °C | Analog Value 1
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Economy Cycle |  |  | Binary Value 30
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | Fan Speed |  | % | Analog Output 2
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-3 | Level 3 | Plantroom | Air Handling Units | 103046 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Min OA Position |  | % | Analog Value 85
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Time Schedule |  |  | Binary Value 40
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | After Hours (old) |  |  | Binary Value 51
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | After Hours (new) |  |  | Binary Value 43
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Filter Status |  |  | Binary Value 44
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Fan Call |  |  | Binary Output 0
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Fan Status |  |  | Binary Value 34
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Fan Fault |  |  | Binary Value 35
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Multiplier SP |  | % | Analog Value 67
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | SA Temp SP |  | °C | Analog Value 13
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | SA Temperature |  | °C | Analog Value 0
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | RA Temperature |  | °C | Analog Value 1
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Economy Cycle |  |  | Binary Value 30
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | Fan Speed |  | % | Analog Output 2
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-3 | Level 3 | Plantroom | Air Handling Units | 103045 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Min OA Position |  | % | Analog Value 85
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Time Schedule |  |  | Binary Value 40
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | After Hours (old) |  |  | Binary Value 51
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | After Hours (new) |  |  | Binary Value 43
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Filter Status |  |  | Binary Value 44
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Fan Call |  |  | Binary Output 0
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Fan Status |  |  | Binary Value 34
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Fan Fault |  |  | Binary Value 35
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Multiplier SP |  | % | Analog Value 67
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | SA Temp SP |  | °C | Analog Value 13
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | SA Temperature |  | °C | Analog Value 0
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | RA Temperature |  | °C | Analog Value 1
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Economy Cycle |  |  | Binary Value 30
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | Fan Speed |  | % | Analog Output 2
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-3 | Level 3 | Plantroom | Air Handling Units | 103047 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Min OA Position |  | % | Analog Value 85
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Time Schedule |  |  | Binary Value 40
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | After Hours (old) |  |  | Binary Value 51
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | After Hours (new) |  |  | Binary Value 43
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Filter Status |  |  | Binary Value 44
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Fan Call |  |  | Binary Output 0
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Fan Status |  |  | Binary Value 34
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Fan Fault |  |  | Binary Value 35
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Multiplier SP |  | % | Analog Value 67
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | SA Temp SP |  | °C | Analog Value 13
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | SA Temperature |  | °C | Analog Value 0
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | RA Temperature |  | °C | Analog Value 1
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Economy Cycle |  |  | Binary Value 30
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | Fan Speed |  | % | Analog Output 2
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-4 | Level 4 | Plantroom | Air Handling Units | 104066 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Min OA Position |  | % | Analog Value 85
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Time Schedule |  |  | Binary Value 40
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | After Hours (old) |  |  | Binary Value 51
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | After Hours (new) |  |  | Binary Value 43
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Filter Status |  |  | Binary Value 44
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Fan Call |  |  | Binary Output 0
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Fan Status |  |  | Binary Value 34
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Fan Fault |  |  | Binary Value 35
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Multiplier SP |  | % | Analog Value 67
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | SA Temp SP |  | °C | Analog Value 13
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | SA Temperature |  | °C | Analog Value 0
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | RA Temperature |  | °C | Analog Value 1
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Economy Cycle |  |  | Binary Value 30
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | Fan Speed |  | % | Analog Output 2
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-4 | Level 4 | Plantroom | Air Handling Units | 104065 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Min OA Position |  | % | Analog Value 85
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Time Schedule |  |  | Binary Value 40
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | After Hours (old) |  |  | Binary Value 51
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | After Hours (new) |  |  | Binary Value 43
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Filter Status |  |  | Binary Value 44
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Fan Call |  |  | Binary Output 0
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Fan Status |  |  | Binary Value 34
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Fan Fault |  |  | Binary Value 35
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Multiplier SP |  | % | Analog Value 67
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | SA Temp SP |  | °C | Analog Value 13
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | SA Temperature |  | °C | Analog Value 0
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | RA Temperature |  | °C | Analog Value 1
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Economy Cycle |  |  | Binary Value 30
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | Fan Speed |  | % | Analog Output 2
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-4 | Level 4 | Plantroom | Air Handling Units | 104067 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Min OA Position |  | % | Analog Value 85
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Time Schedule |  |  | Binary Value 40
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | After Hours (old) |  |  | Binary Value 51
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | After Hours (new) |  |  | Binary Value 43
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Filter Status |  |  | Binary Value 44
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Fan Call |  |  | Binary Output 0
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Fan Status |  |  | Binary Value 34
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Fan Fault |  |  | Binary Value 35
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Multiplier SP |  | % | Analog Value 67
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | SA Temp SP |  | °C | Analog Value 13
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | SA Temperature |  | °C | Analog Value 0
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | RA Temperature |  | °C | Analog Value 1
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Economy Cycle |  |  | Binary Value 30
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | Fan Speed |  | % | Analog Output 2
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-5 | Level 5 | Plantroom | Air Handling Units | 205006 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Min OA Position |  | % | Analog Value 85
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Time Schedule |  |  | Binary Value 40
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | After Hours (old) |  |  | Binary Value 51
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | After Hours (new) |  |  | Binary Value 43
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Filter Status |  |  | Binary Value 44
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Fan Call |  |  | Binary Output 0
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Fan Status |  |  | Binary Value 34
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Fan Fault |  |  | Binary Value 35
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Multiplier SP |  | % | Analog Value 67
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | SA Temp SP |  | °C | Analog Value 13
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | SA Temperature |  | °C | Analog Value 0
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | RA Temperature |  | °C | Analog Value 1
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Economy Cycle |  |  | Binary Value 30
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | Fan Speed |  | % | Analog Output 2
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-5 | Level 5 | Plantroom | Air Handling Units | 205005 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Min OA Position |  | % | Analog Value 85
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Time Schedule |  |  | Binary Value 40
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | After Hours (old) |  |  | Binary Value 51
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | After Hours (new) |  |  | Binary Value 43
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Filter Status |  |  | Binary Value 44
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Fan Call |  |  | Binary Output 0
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Fan Status |  |  | Binary Value 34
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Fan Fault |  |  | Binary Value 35
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Multiplier SP |  | % | Analog Value 67
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | SA Temp SP |  | °C | Analog Value 13
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | SA Temperature |  | °C | Analog Value 0
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | RA Temperature |  | °C | Analog Value 1
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Economy Cycle |  |  | Binary Value 30
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | Fan Speed |  | % | Analog Output 2
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-5 | Level 5 | Plantroom | Air Handling Units | 205007 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Min OA Position |  | % | Analog Value 85
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Time Schedule |  |  | Binary Value 40
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | After Hours (old) |  |  | Binary Value 51
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | After Hours (new) |  |  | Binary Value 43
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Filter Status |  |  | Binary Value 44
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Fan Call |  |  | Binary Output 0
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Fan Status |  |  | Binary Value 34
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Fan Fault |  |  | Binary Value 35
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Multiplier SP |  | % | Analog Value 67
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | SA Temp SP |  | °C | Analog Value 13
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | SA Temperature |  | °C | Analog Value 0
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | RA Temperature |  | °C | Analog Value 1
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Economy Cycle |  |  | Binary Value 30
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | Fan Speed |  | % | Analog Output 2
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-6 | Level 6 | Plantroom | Air Handling Units | 206026 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Min OA Position |  | % | Analog Value 85
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Time Schedule |  |  | Binary Value 40
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | After Hours (old) |  |  | Binary Value 51
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | After Hours (new) |  |  | Binary Value 43
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Filter Status |  |  | Binary Value 44
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Fan Call |  |  | Binary Output 0
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Fan Status |  |  | Binary Value 34
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Fan Fault |  |  | Binary Value 35
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Multiplier SP |  | % | Analog Value 67
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | SA Temp SP |  | °C | Analog Value 13
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | SA Temperature |  | °C | Analog Value 0
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | RA Temperature |  | °C | Analog Value 1
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Economy Cycle |  |  | Binary Value 30
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | Fan Speed |  | % | Analog Output 2
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-6 | Level 6 | Plantroom | Air Handling Units | 206025 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Min OA Position |  | % | Analog Value 85
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Time Schedule |  |  | Binary Value 40
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | After Hours (old) |  |  | Binary Value 51
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | After Hours (new) |  |  | Binary Value 43
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Filter Status |  |  | Binary Value 44
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Fan Call |  |  | Binary Output 0
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Fan Status |  |  | Binary Value 34
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Fan Fault |  |  | Binary Value 35
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Multiplier SP |  | % | Analog Value 67
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | SA Temp SP |  | °C | Analog Value 13
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | SA Temperature |  | °C | Analog Value 0
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | RA Temperature |  | °C | Analog Value 1
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Economy Cycle |  |  | Binary Value 30
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | Fan Speed |  | % | Analog Output 2
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-6 | Level 6 | Plantroom | Air Handling Units | 206027 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Min OA Position |  | % | Analog Value 85
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Time Schedule |  |  | Binary Value 40
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | After Hours (old) |  |  | Binary Value 51
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | After Hours (new) |  |  | Binary Value 43
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Filter Status |  |  | Binary Value 44
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Fan Call |  |  | Binary Output 0
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Fan Status |  |  | Binary Value 34
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Fan Fault |  |  | Binary Value 35
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Multiplier SP |  | % | Analog Value 67
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | SA Temp SP |  | °C | Analog Value 13
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | SA Temperature |  | °C | Analog Value 0
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | RA Temperature |  | °C | Analog Value 1
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Economy Cycle |  |  | Binary Value 30
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | Fan Speed |  | % | Analog Output 2
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-7 | Level 7 | Plantroom | Air Handling Units | 207046 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Min OA Position |  | % | Analog Value 85
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Time Schedule |  |  | Binary Value 40
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | After Hours (old) |  |  | Binary Value 51
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | After Hours (new) |  |  | Binary Value 43
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Filter Status |  |  | Binary Value 44
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Fan Call |  |  | Binary Output 0
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Fan Status |  |  | Binary Value 34
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Fan Fault |  |  | Binary Value 35
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Multiplier SP |  | % | Analog Value 67
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | SA Temp SP |  | °C | Analog Value 13
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | SA Temperature |  | °C | Analog Value 0
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | RA Temperature |  | °C | Analog Value 1
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Economy Cycle |  |  | Binary Value 30
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | Fan Speed |  | % | Analog Output 2
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-7 | Level 7 | Plantroom | Air Handling Units | 207045 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Min OA Position |  | % | Analog Value 85
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Time Schedule |  |  | Binary Value 40
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | After Hours (old) |  |  | Binary Value 51
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | After Hours (new) |  |  | Binary Value 43
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Filter Status |  |  | Binary Value 44
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Fan Call |  |  | Binary Output 0
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Fan Status |  |  | Binary Value 34
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Fan Fault |  |  | Binary Value 35
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Multiplier SP |  | % | Analog Value 67
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | SA Temp SP |  | °C | Analog Value 13
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | SA Temperature |  | °C | Analog Value 0
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | RA Temperature |  | °C | Analog Value 1
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Economy Cycle |  |  | Binary Value 30
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | Fan Speed |  | % | Analog Output 2
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-7 | Level 7 | Plantroom | Air Handling Units | 207047 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Min OA Position |  | % | Analog Value 85
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Time Schedule |  |  | Binary Value 40
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | After Hours (old) |  |  | Binary Value 51
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | After Hours (new) |  |  | Binary Value 43
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Filter Status |  |  | Binary Value 44
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Fan Call |  |  | Binary Output 0
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Fan Status |  |  | Binary Value 34
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Fan Fault |  |  | Binary Value 35
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Multiplier SP |  | % | Analog Value 67
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | SA Temp SP |  | °C | Analog Value 13
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | SA Temperature |  | °C | Analog Value 0
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | RA Temperature |  | °C | Analog Value 1
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Economy Cycle |  |  | Binary Value 30
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | Fan Speed |  | % | Analog Output 2
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-8 | Level 8 | Plantroom | Air Handling Units | 208066 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Min OA Position |  | % | Analog Value 85
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Time Schedule |  |  | Binary Value 40
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | After Hours (old) |  |  | Binary Value 51
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | After Hours (new) |  |  | Binary Value 43
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Filter Status |  |  | Binary Value 44
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Fan Call |  |  | Binary Output 0
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Fan Status |  |  | Binary Value 34
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Fan Fault |  |  | Binary Value 35
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Multiplier SP |  | % | Analog Value 67
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | SA Temp SP |  | °C | Analog Value 13
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | SA Temperature |  | °C | Analog Value 0
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | RA Temperature |  | °C | Analog Value 1
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Economy Cycle |  |  | Binary Value 30
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | Fan Speed |  | % | Analog Output 2
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-8 | Level 8 | Plantroom | Air Handling Units | 208065 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Min OA Position |  | % | Analog Value 85
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Time Schedule |  |  | Binary Value 40
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | After Hours (old) |  |  | Binary Value 51
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | After Hours (new) |  |  | Binary Value 43
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Filter Status |  |  | Binary Value 44
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Fan Call |  |  | Binary Output 0
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Fan Status |  |  | Binary Value 34
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Fan Fault |  |  | Binary Value 35
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Multiplier SP |  | % | Analog Value 67
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | SA Temp SP |  | °C | Analog Value 13
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | SA Temperature |  | °C | Analog Value 0
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | RA Temperature |  | °C | Analog Value 1
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Economy Cycle |  |  | Binary Value 30
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | Fan Speed |  | % | Analog Output 2
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-8 | Level 8 | Plantroom | Air Handling Units | 208067 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Min OA Position |  | % | Analog Value 85
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Time Schedule |  |  | Binary Value 40
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | After Hours (old) |  |  | Binary Value 51
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | After Hours (new) |  |  | Binary Value 43
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Filter Status |  |  | Binary Value 44
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Fan Call |  |  | Binary Output 0
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Fan Status |  |  | Binary Value 34
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Fan Fault |  |  | Binary Value 35
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Multiplier SP |  | % | Analog Value 67
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | SA Temp SP |  | °C | Analog Value 13
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | SA Temperature |  | °C | Analog Value 0
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | RA Temperature |  | °C | Analog Value 1
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Economy Cycle |  |  | Binary Value 30
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | Fan Speed |  | % | Analog Output 2
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-9 | Level 9 | Plantroom | Air Handling Units | 309006 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Min OA Position |  | % | Analog Value 85
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Time Schedule |  |  | Binary Value 40
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | After Hours (old) |  |  | Binary Value 51
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | After Hours (new) |  |  | Binary Value 43
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Filter Status |  |  | Binary Value 44
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Fan Call |  |  | Binary Output 0
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Fan Status |  |  | Binary Value 34
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Fan Fault |  |  | Binary Value 35
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Multiplier SP |  | % | Analog Value 67
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | SA Temp SP |  | °C | Analog Value 13
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | SA Temperature |  | °C | Analog Value 0
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | RA Temperature |  | °C | Analog Value 1
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Economy Cycle |  |  | Binary Value 30
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | Fan Speed |  | % | Analog Output 2
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-9 | Level 9 | Plantroom | Air Handling Units | 309005 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Min OA Position |  | % | Analog Value 85
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Time Schedule |  |  | Binary Value 40
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | After Hours (old) |  |  | Binary Value 51
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | After Hours (new) |  |  | Binary Value 43
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Filter Status |  |  | Binary Value 44
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Fan Call |  |  | Binary Output 0
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Fan Status |  |  | Binary Value 34
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Fan Fault |  |  | Binary Value 35
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Multiplier SP |  | % | Analog Value 67
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | SA Temp SP |  | °C | Analog Value 13
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | SA Temperature |  | °C | Analog Value 0
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | RA Temperature |  | °C | Analog Value 1
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Economy Cycle |  |  | Binary Value 30
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | Fan Speed |  | % | Analog Output 2
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-9 | Level 9 | Plantroom | Air Handling Units | 309007 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Min OA Position |  | % | Analog Value 85
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Time Schedule |  |  | Binary Value 40
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | After Hours (old) |  |  | Binary Value 51
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | After Hours (new) |  |  | Binary Value 43
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Filter Status |  |  | Binary Value 44
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Fan Call |  |  | Binary Output 0
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Fan Status |  |  | Binary Value 34
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Fan Fault |  |  | Binary Value 35
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Multiplier SP |  | % | Analog Value 67
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | SA Temp SP |  | °C | Analog Value 13
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | SA Temperature |  | °C | Analog Value 0
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | RA Temperature |  | °C | Analog Value 1
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Economy Cycle |  |  | Binary Value 30
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | Fan Speed |  | % | Analog Output 2
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-10 | Level 10 | Plantroom | Air Handling Units | 310026 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Min OA Position |  | % | Analog Value 85
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Time Schedule |  |  | Binary Value 40
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | After Hours (old) |  |  | Binary Value 51
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | After Hours (new) |  |  | Binary Value 43
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Filter Status |  |  | Binary Value 44
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Fan Call |  |  | Binary Output 0
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Fan Status |  |  | Binary Value 34
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Fan Fault |  |  | Binary Value 35
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Multiplier SP |  | % | Analog Value 67
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | SA Temp SP |  | °C | Analog Value 13
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | SA Temperature |  | °C | Analog Value 0
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | RA Temperature |  | °C | Analog Value 1
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Economy Cycle |  |  | Binary Value 30
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | Fan Speed |  | % | Analog Output 2
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-10 | Level 10 | Plantroom | Air Handling Units | 310025 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Min OA Position |  | % | Analog Value 85
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Time Schedule |  |  | Binary Value 40
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | After Hours (old) |  |  | Binary Value 51
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | After Hours (new) |  |  | Binary Value 43
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Filter Status |  |  | Binary Value 44
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Fan Call |  |  | Binary Output 0
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Fan Status |  |  | Binary Value 34
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Fan Fault |  |  | Binary Value 35
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Multiplier SP |  | % | Analog Value 67
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | SA Temp SP |  | °C | Analog Value 13
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | SA Temperature |  | °C | Analog Value 0
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | RA Temperature |  | °C | Analog Value 1
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Economy Cycle |  |  | Binary Value 30
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | Fan Speed |  | % | Analog Output 2
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-10 | Level 10 | Plantroom | Air Handling Units | 310027 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Min OA Position |  | % | Analog Value 85
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Time Schedule |  |  | Binary Value 40
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | After Hours (old) |  |  | Binary Value 51
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | After Hours (new) |  |  | Binary Value 43
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Filter Status |  |  | Binary Value 44
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Fan Call |  |  | Binary Output 0
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Fan Status |  |  | Binary Value 34
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Fan Fault |  |  | Binary Value 35
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Multiplier SP |  | % | Analog Value 67
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | SA Temp SP |  | °C | Analog Value 13
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | SA Temperature |  | °C | Analog Value 0
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | RA Temperature |  | °C | Analog Value 1
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Economy Cycle |  |  | Binary Value 30
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | Fan Speed |  | % | Analog Output 2
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-11 | Level 11 | Plantroom | Air Handling Units | 311046 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Min OA Position |  | % | Analog Value 85
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Time Schedule |  |  | Binary Value 40
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | After Hours (old) |  |  | Binary Value 51
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | After Hours (new) |  |  | Binary Value 43
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Filter Status |  |  | Binary Value 44
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Fan Call |  |  | Binary Output 0
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Fan Status |  |  | Binary Value 34
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Fan Fault |  |  | Binary Value 35
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Multiplier SP |  | % | Analog Value 67
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | SA Temp SP |  | °C | Analog Value 13
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | SA Temperature |  | °C | Analog Value 0
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | RA Temperature |  | °C | Analog Value 1
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Economy Cycle |  |  | Binary Value 30
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | Fan Speed |  | % | Analog Output 2
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-11 | Level 11 | Plantroom | Air Handling Units | 311045 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Min OA Position |  | % | Analog Value 85
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Time Schedule |  |  | Binary Value 40
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | After Hours (old) |  |  | Binary Value 51
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | After Hours (new) |  |  | Binary Value 43
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Filter Status |  |  | Binary Value 44
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Fan Call |  |  | Binary Output 0
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Fan Status |  |  | Binary Value 34
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Fan Fault |  |  | Binary Value 35
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Multiplier SP |  | % | Analog Value 67
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | SA Temp SP |  | °C | Analog Value 13
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | SA Temperature |  | °C | Analog Value 0
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | RA Temperature |  | °C | Analog Value 1
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Economy Cycle |  |  | Binary Value 30
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | Fan Speed |  | % | Analog Output 2
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-11 | Level 11 | Plantroom | Air Handling Units | 311047 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Min OA Position |  | % | Analog Value 85
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Time Schedule |  |  | Binary Value 40
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | After Hours (old) |  |  | Binary Value 51
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | After Hours (new) |  |  | Binary Value 43
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Filter Status |  |  | Binary Value 44
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Fan Call |  |  | Binary Output 0
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Fan Status |  |  | Binary Value 34
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Fan Fault |  |  | Binary Value 35
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Multiplier SP |  | % | Analog Value 67
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | SA Temp SP |  | °C | Analog Value 13
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | SA Temperature |  | °C | Analog Value 0
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | RA Temperature |  | °C | Analog Value 1
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Economy Cycle |  |  | Binary Value 30
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | Fan Speed |  | % | Analog Output 2
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-12 | Level 12 | Plantroom | Air Handling Units | 312066 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Min OA Position |  | % | Analog Value 85
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Time Schedule |  |  | Binary Value 40
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | After Hours (old) |  |  | Binary Value 51
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | After Hours (new) |  |  | Binary Value 43
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Filter Status |  |  | Binary Value 44
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Fan Call |  |  | Binary Output 0
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Fan Status |  |  | Binary Value 34
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Fan Fault |  |  | Binary Value 35
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Multiplier SP |  | % | Analog Value 67
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | SA Temp SP |  | °C | Analog Value 13
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | SA Temperature |  | °C | Analog Value 0
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | RA Temperature |  | °C | Analog Value 1
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Economy Cycle |  |  | Binary Value 30
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | Fan Speed |  | % | Analog Output 2
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-12 | Level 12 | Plantroom | Air Handling Units | 312065 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Min OA Position |  | % | Analog Value 85
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Time Schedule |  |  | Binary Value 40
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | After Hours (old) |  |  | Binary Value 51
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | After Hours (new) |  |  | Binary Value 43
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Filter Status |  |  | Binary Value 44
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Fan Call |  |  | Binary Output 0
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Fan Status |  |  | Binary Value 34
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Fan Fault |  |  | Binary Value 35
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Multiplier SP |  | % | Analog Value 67
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | SA Temp SP |  | °C | Analog Value 13
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | SA Temperature |  | °C | Analog Value 0
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | RA Temperature |  | °C | Analog Value 1
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Economy Cycle |  |  | Binary Value 30
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | Fan Speed |  | % | Analog Output 2
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-12 | Level 12 | Plantroom | Air Handling Units | 312067 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Min OA Position |  | % | Analog Value 85
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Time Schedule |  |  | Binary Value 40
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | After Hours (old) |  |  | Binary Value 51
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | After Hours (new) |  |  | Binary Value 43
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Filter Pressure |  | Pa | Analog Value 4
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Filter Status |  |  | Binary Value 44
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Fan Call |  |  | Binary Output 0
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Fan Status |  |  | Binary Value 34
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Fan Fault |  |  | Binary Value 35
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Multiplier SP |  | % | Analog Value 67
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Desired VAV Air |  | L/s | Analog Value 68
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Current VAV Air |  | L/s | Analog Value 69
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | SA Temp SP |  | °C | Analog Value 13
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | SA Temperature |  | °C | Analog Value 0
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | HHW Valve Cmd |  |  | Analog Output 1
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | RA Temperature |  | °C | Analog Value 1
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Economy Cycle |  |  | Binary Value 30
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | Fan Speed |  | % | Analog Output 2
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-13 | Level 13 | Plantroom | Air Handling Units | 413006 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Min OA Position |  | % | Analog Value 85
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Time Schedule |  |  | Binary Value 40
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | After Hours (old) |  |  | Binary Value 51
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | After Hours (new) |  |  | Binary Value 43
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Filter Pressure |  | Pa | Analog Value 4
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Filter Status |  |  | Binary Value 44
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Fan Call |  |  | Binary Output 0
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Fan Status |  |  | Binary Value 34
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Fan Fault |  |  | Binary Value 35
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Multiplier SP |  | % | Analog Value 67
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Desired VAV Air |  | L/s | Analog Value 68
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Current VAV Air |  | L/s | Analog Value 69
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | SA Temp SP |  | °C | Analog Value 13
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | SA Temperature |  | °C | Analog Value 0
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | HHW Valve Cmd |  |  | Analog Output 1
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | RA Temperature |  | °C | Analog Value 1
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Economy Cycle |  |  | Binary Value 30
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | Fan Speed |  | % | Analog Output 2
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-13 | Level 13 | Plantroom | Air Handling Units | 413005 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Min OA Position |  | % | Analog Value 85
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | OA Damper Cmd |  | % | Analog Output 5
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | RA Damper Cmd |  | % | Analog Output 3
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Time Schedule |  |  | Binary Value 40
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | After Hours (old) |  |  | Binary Value 51
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | After Hours (new) |  |  | Binary Value 43
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Filter Pressure |  | Pa | Analog Value 4
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Filter Status |  |  | Binary Value 44
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Fan Call |  |  | Binary Output 0
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Fan Status |  |  | Binary Value 34
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Fan Fault |  |  | Binary Value 35
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Total Runhours |  | Hrs | Analog Value 34
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Multiplier SP |  | % | Analog Value 67
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Desired VAV Air |  | L/s | Analog Value 68
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Current VAV Air |  | L/s | Analog Value 69
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | SA Temp SP |  | °C | Analog Value 13
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | SA Temperature |  | °C | Analog Value 0
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | HHW Valve Cmd |  |  | Analog Output 1
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | RA Temperature |  | °C | Analog Value 1
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Measured CO2 |  | ppm | Analog Value 10
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Economy Cycle |  |  | Binary Value 30
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | Fan Speed |  | % | Analog Output 2
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N-13 | Level 13 | Plantroom | Air Handling Units | 413007 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Min OA Position |  | % | Analog Value 85
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | OA Damper Cmd |  | % | Analog Output 5
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | OA Damper Fdbk |  | % | Analog Input 7
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | RA Damper Cmd |  | % | Analog Output 3
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | RA Damper Fdbk |  | % | Analog Input 8
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Time Schedule |  |  | Binary Value 40
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | After Hours (new) |  |  | Binary Value 43
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Avg Zone Temp |  | °C | Analog Value 57
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Filter Status |  |  | Binary Value 44
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Fan Call |  |  | Binary Output 0
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Fan Status |  |  | Binary Value 34
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Fan Fault |  |  | Binary Value 35
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Total Runhours |  | Hrs | Analog Value 34
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Static Pressure SP |  | Pa | Analog Value 38
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Static Pressure |  | Pa | Analog Value 45
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Zone Setpoint |  | °C | Analog Value 15
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Dynamic SA SP |  | °C | Analog Value 23
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | SA Temp SP |  | °C | Analog Value 13
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | SA Temperature |  | °C | Analog Value 0
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | CHW Valve Cmd |  |  | Analog Output 0
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | HHW Valve Cmd |  | % | Analog Output 1
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | RA Temperature |  | °C | Analog Value 1
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Measured CO2 |  | ppm | Analog Value 10
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Economy Cycle |  |  | Binary Value 30
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Fan Speed |  | % | Analog Output 2
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | CHW Supply Temp |  | °C | Analog Input 6
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Warm Up Cycle |  |  | Binary Value 41
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Cool Down Cycle |  |  | Binary Value 42
AHU-E-14 | Level 14 | Plantroom | Air Handling Units | 415028 | Warm Up SA SP |  | °C | Binary Value 54
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Min OA Position |  | % | Analog Value 85
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | OA Damper Cmd |  | % | Analog Output 5
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | OA Damper Fdbk |  | % | Analog Input 7
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | RA Damper Cmd |  | % | Analog Output 3
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | RA Damper Fdbk |  | % | Analog Input 8
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Time Schedule |  |  | Binary Value 40
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | After Hours (new) |  |  | Binary Value 43
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Avg Zone Temp |  | °C | Analog Value 57
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Filter Status |  |  | Binary Value 44
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Fan Call |  |  | Binary Output 0
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Fan Status |  |  | Binary Value 34
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Fan Fault |  |  | Binary Value 35
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Total Runhours |  | Hrs | Analog Value 34
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Static Pressure SP |  | Pa | Analog Value 38
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Static Pressure |  | Pa | Analog Value 45
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Zone Setpoint |  | °C | Analog Value 15
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Dynamic SA SP |  | °C | Analog Value 23
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | SA Temp SP |  | °C | Analog Value 13
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | SA Temperature |  | °C | Analog Value 0
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | CHW Valve Cmd |  |  | Analog Output 0
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | HHW Valve Cmd |  | % | Analog Output 1
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | RA Temperature |  | °C | Analog Value 1
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Measured CO2 |  | ppm | Analog Value 10
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Economy Cycle |  |  | Binary Value 30
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Fan Speed |  | % | Analog Output 2
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | CHW Supply Temp |  | °C | Analog Input 6
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Warm Up Cycle |  |  | Binary Value 41
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Cool Down Cycle |  |  | Binary Value 42
AHU-C-14 | Level 14 | Plantroom | Air Handling Units | 415027 | Warm Up SA SP |  | °C | Binary Value 54
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Min OA Position |  | % | Analog Value 85
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | OA Damper Cmd |  | % | Analog Output 5
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | RA Damper Cmd |  | % | Analog Output 3
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | RA Damper Fdbk |  | % | Analog Input 8
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Relief Damper Fdbk |  |  | Binary Value 2
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Time Schedule |  |  | Binary Value 40
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | After Hours (new) |  |  | Binary Value 43
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Filter Status |  |  | Binary Value 44
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Fan Call |  |  | Binary Output 0
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Fan Call (Auto) |  |  | Binary Output 0, Priority array idx 8
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Fan Status |  |  | Binary Value 34
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Fan Fault |  |  | Binary Value 35
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Total Runhours |  | Hrs | Analog Value 34
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Static Pressure SP |  | Pa | Analog Value 38
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Static Pressure |  | Pa | Analog Value 45
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Zone Setpoint |  | °C | Analog Value 15
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Dynamic SA SP |  | °C | Analog Value 23
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | SA Temp SP |  | °C | Analog Value 13
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | SA Temp SP (display) |  | °C | Analog Value 3
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | SA Temperature |  | °C | Analog Value 0
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | HHW Valve Cmd |  | % | Analog Output 1
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | RA Temperature |  | °C | Analog Value 1
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Measured CO2 |  | ppm | Analog Value 10
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Economy Cycle |  |  | Binary Value 30
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Fan Speed |  | % | Analog Output 2
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | CHW Supply Temp |  | °C | Analog Input 6
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Warm Up Cycle |  |  | Binary Value 41
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Cool Down Cycle |  |  | Binary Value 42
AHU-N2-14 | Level 14 | Plantroom | Air Handling Units | 415026 | Warm Up SA SP |  | °C | Binary Value 54
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | OA Damper Cmd |  | % | Analog Output 5
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | OA Damper Fdbk |  | % | Analog Input 7
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Time Schedule |  |  | Binary Value 40
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | After Hours (new) |  |  | Binary Value 43
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Avg Zone Temp |  | °C | Analog Value 57
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Filter Status |  |  | Binary Value 44
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Fan Call |  |  | Binary Output 0
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Fan Status |  |  | Binary Value 34
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Fan Fault |  |  | Binary Value 35
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Fan Mismatch Fault |  |  | Binary Value 20
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Total Runhours |  | Hrs | Analog Value 34
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Zone Setpoint |  | °C | Analog Value 14
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | SA Temp SP |  | °C | Analog Value 13
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | SA Temperature |  | °C | Analog Value 0
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | CHW Valve Cmd |  |  | Analog Output 0
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | CHW Valve Fdbk |  | % | Analog Input 0
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | HHW Valve Cmd |  | % | Analog Output 1
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | HHW Valve Fdbk |  | % | Analog Input 1
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Fan Speed |  | % | Analog Output 2
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | Warm Up SA SP |  | °C | Binary Value 54
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | CHW Inlet Temp |  | °C | Analog Input 5
AHU-N1-14 | Level 14 | Plantroom | Air Handling Units | 415025 | CHW Supply Temp |  | °C | Analog Input 6
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Low CHW Temp (Freeze Lockout) |  |  | Device 9901, Binary Value 13
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | High Condensing Pressure |  |  | Device 9901, Binary Value 22
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Low Evaporator Pressure |  |  | Device 9901, Binary Value 23
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Compressor ON/OFF |  |  | Device 9901, Binary Value 28
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Chiller Running Status |  |  | Device 9901, Binary Value 45
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Common Alarm |  |  | Device 9901, Binary Value 46
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | LCW Sensor Fault |  |  | Device 9901, Binary Value 58
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Chiller Controller Message |  |  | Device 9901, Analog Value 1014
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | CHW Setpoint |  | °C | Device 9901, Analog Value 3
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Entering CHW Temp |  | °C | Device 9901, Analog Value 7
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Leaving CHW Temp |  | °C | Device 9901, Analog Value 8
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Entering CCW Temp |  | °C | Device 9901, Analog Value 9
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Leaving CCW Temp |  | °C | Device 9901, Analog Value 10
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Compressor Demand |  | % | Device 9901, Analog Value 11
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | System kW Total |  | kW's | Device 9901, Analog Value 15
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Chiller Demand Limit |  | % | Device 9901, Analog Value 18
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | C.O.P. |  |  | Device 9901, Analog Value 1010
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Call |  |  | Device 415036, Binary Output 2
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Status |  |  | Device 415036, Binary Value 38
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Fault |  |  | Device 415036, Binary Value 39
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Mismatch Alarm Delay |  | sec | Device 415036, Analog Value 15
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | Design Pressure Drop CHW |  | Kpa | Device 4000, Analog Value 313
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | System On |  |  | Device 9901, Binary Value 0
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | CHW Setpoint (BACnet) |  | °C | Device 9901, Analog Value 1
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | SP Offset |  | °C | Device 9901, Analog Value 4
Chiller-1 | Level 15 | Plantroom | Chiller | 9901 | CHW Actual Setpoint |  | °C | Device 9901, Analog Value 5
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Remote Call/Stop |  |  | Device 9902, Binary Value 0
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Evap Flow Status |  |  | Device 9902, Binary Value 3
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Cond Flow Status |  |  | Device 9902, Binary Value 4
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Temp Remote Reset |  |  | Device 9902, Binary Value 6
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Unit Call/Stop |  |  | Device 9902, Binary Value 8
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Phase Monitor Alarm |  |  | Device 9902, Binary Value 9
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Evap Freeze Protect |  |  | Device 9902, Binary Value 10
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | No Cond Water Flow Fault |  |  | Device 9902, Binary Value 11
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Alarm Flag |  |  | Device 9902, Binary Value 1
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Local Setpoint |  | °C | Device 9902, Analog Value 0
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Evap Entering Temp |  | °C | Device 9902, Analog Value 1
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Evap Leaving Temp |  | °C | Device 9902, Analog Value 2
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Cond Entering Temp |  | °C | Device 9902, Analog Value 3
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Cond Leaving Temp |  | °C | Device 9902, Analog Value 4
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Capacity |  | % | Device 9902, Analog Value 5
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | BMS Start/Stop |  |  | Device 9902, Analog Value 6
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Call |  |  | Device 415037, Binary Output 2
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Status |  |  | Device 415037, Binary Value 38
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Fault |  |  | Device 415037, Binary Value 39
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Chiller Run |  |  | Device 415037, Binary Value 47
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Evap Pump Status |  |  | Device 415037, Binary Value 48
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Cond Pump Status |  |  | Device 415037, Binary Value 49
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Design Pressure Drop CHW |  | Kpa | Device 4000, Analog Value 314
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Chiller 2 on delay |  | secs | Device 415037, Analog Value 16
Chiller-2 | Level 15 | Plantroom | Chiller | 9902 | Mismatch Alarm Delay |  | sec | Device 415037, Analog Value 15
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Call |  |  | Device 415036, Binary Output 0
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Status |  |  | Device 415036, Binary Value 34
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Fault |  |  | Device 415036, Binary Value 35
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Mismatch |  |  | Device 415036, Binary Value 20
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Runtime |  | hrs | Device 415036, Analog Value 34
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Pump Speed |  | % | Device 415036, Analog Output 2
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | CHWP-1 Field DP SP |  | Kpa | Device 415037, Analog Value 36
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Field Differential Pressure |  | KPa | Device 415037, Analog Input 0
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Field Differential Pressure SP |  | kPa | Device 415037, Analog Value 37
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Kp |  |  | Device 415037, Analog Value 30
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Ki |  |  | Device 415037, Analog Value 31
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Min Speed |  | % | Device 415036, Analog Value 21
CHWP-1 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415036 | Pump Speed (ctrl) |  | % | Device 415036, Analog Output 2
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Call |  |  | Device 415037, Binary Output 0
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Status |  |  | Device 415037, Binary Value 34
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Fault |  |  | Device 415037, Binary Value 35
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Mismatch |  |  | Device 415037, Binary Value 20
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Runtime |  | hrs | Device 415037, Analog Value 34
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Pump Speed |  | % | Device 415037, Analog Output 2
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | CHWP-2 Field DP SP |  | Kpa | Device 415037, Analog Value 38
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Field Differential Pressure |  | KPa | Device 415037, Analog Input 0
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Field Differential Pressure SP |  |  | Device 415037, Analog Value 37
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Kp |  |  | Device 415037, Analog Value 30
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Ki |  |  | Device 415037, Analog Value 31
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Min Speed |  | % | Device 415037, Analog Value 21
CHWP-2 | Level 15 | Plantroom | Primary Chilled Water Pumps | 415037 | Pump Speed (ctrl) |  | % | Device 415037, Analog Output 2
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Call |  |  | Device 415036, Binary Output 1
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Status |  |  | Device 415036, Binary Value 36
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Fault |  |  | Device 415036, Binary Value 37
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Mismatch |  |  | Device 415036, Binary Value 21
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Runtime |  | hrs | Device 415036, Analog Value 35
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Pump Speed |  | % | Device 415036, Analog Output 3
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Delay on Call |  | Secs | Device 415036, Analog Value 22
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Chiller-1 Differential Pressure |  | KPa | Device 415036, Analog Input 2
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Chiller-1 Differential Pressure SP |  | KPa | Device 415036, Analog Value 23
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Kp |  |  | Device 415036, Analog Value 24
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Ki |  |  | Device 415036, Analog Value 25
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Min Speed |  | % | Device 415036, Analog Value 26
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | Pump Speed (ctrl) |  | % | Device 415036, Analog Output 3
CCWP-1 | Level 15 | Plantroom | Condenser Water Pumps | 415036 | 120.0 |  |  | Device 4000, Analog Value 312
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Call |  |  | Device 415037, Binary Output 1
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Status |  |  | Device 415037, Binary Value 36
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Fault |  |  | Device 415037, Binary Value 37
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Mismatch |  |  | Device 415037, Binary Value 21
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Runtime |  | hrs | Device 415037, Analog Value 35
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Pump Speed |  | Hz | Device 415037, Analog Output 3
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Delay on Call |  |  | Device 415037, Analog Value 22
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Chiller-2 Differential Pressure |  | KPa | Device 415037, Analog Input 2
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Chiller-2 Differential Pressure SP |  | KPa | Device 415037, Analog Value 23
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Kp |  |  | Device 415037, Analog Value 24
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Ki |  |  | Device 415037, Analog Value 25
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Min Speed |  | % | Device 415037, Analog Value 26
CCWP-2 | Level 15 | Plantroom | Condenser Water Pumps | 415037 | Pump Speed (ctrl) |  | % | Device 415037, Analog Output 3
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Call |  |  | Device 415034, Binary Output 0
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Status |  |  | Device 415034, Binary Value 34
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Fault |  |  | Device 415034, Binary Value 35
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Mismatch |  |  | Device 415034, Binary Value 20
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Runtime |  | hrs | Device 415034, Analog Value 34
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | CT Leaving Temperature |  | °C | Device 415034, Analog Input 0
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | CT System Fault |  |  | Device 415034, Binary Value 39
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Common Entering Temperature |  | °C | Device 415034, Analog Input 2
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Common Leaving Temperature |  | °C | Device 415034, Analog Input 1
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Common Leaving Temperature SP |  | °C | Device 415034, Analog Value 23
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Kp |  |  | Device 415034, Analog Value 24
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Ki |  |  | Device 415034, Analog Value 25
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Min Speed |  | % | Device 415034, Analog Value 26
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Speed |  | % | Device 415034, Analog Output 2
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Active |  |  | Device 415034, Binary Value 44
Cooling Tower-1 | Roof | Plantroom | Cooling Tower | 415034 | Other CT Leaving Temp |  | °C | Device 415034, Analog Input 3
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Call |  |  | Device 415034, Binary Output 0
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Status |  |  | Device 415034, Binary Value 34
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Fault |  |  | Device 415034, Binary Value 35
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Mismatch |  |  | Device 415034, Binary Value 20
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Runtime |  | hrs | Device 415034, Analog Value 34
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | CT Leaving Temperature |  | °C | Device 415034, Analog Input 0
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | CT System Fault |  |  | Device 415034, Binary Value 39
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Common Entering Temperature |  | °C | Device 415034, Analog Input 2
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Common Leaving Temperature |  | °C | Device 415034, Analog Input 1
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Common Leaving Temperature SP |  | °C | Device 415034, Analog Value 23
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Kp |  |  | Device 415034, Analog Value 24
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Ki |  |  | Device 415034, Analog Value 25
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Min Speed |  | % | Device 415034, Analog Value 26
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Speed |  | % | Device 415034, Analog Output 2
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Active |  |  | Device 415034, Binary Value 44
Cooling Tower-2 | Roof | Plantroom | Cooling Tower | 415034 | Other CT Leaving Temp |  | °C | Device 415034, Analog Input 3
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Call |  |  | Device 415033, Binary Output 0
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Status |  |  | Device 415033, Binary Value 34
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Fault |  |  | Device 415033, Binary Value 35
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Mismatch |  |  | Device 415033, Binary Value 20
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Runtime |  |  | Device 415033, Analog Value 34
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Speed |  |  | Device 415033, Analog Output 2
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | System Fault |  |  | Device 415033, Binary Value 39
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Call Setpoint |  | °C | Device 415033, Analog Value 36
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Current Supply Temp |  | °C | Device 415032, Analog Input 0
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Primary Return Temperature |  | °C | Device 415033, Analog Input 0
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Primary Return Temperature SP |  | °C | Device 415033, Analog Value 23
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Kp |  |  | Device 415033, Analog Value 24
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Ki |  |  | Device 415033, Analog Value 25
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Min Speed |  | % | Device 415033, Analog Value 26
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Max Speed |  | % | Device 415033, Analog Value 27
TSCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Speed (ctrl) |  | % | Device 415033, Analog Output 2
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Call |  |  | Device 415033, Binary Output 0
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Status |  |  | Device 415033, Binary Value 34
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Fault |  |  | Device 415033, Binary Value 35
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Mismatch |  |  | Device 415033, Binary Value 20
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Runtime |  |  | Device 415033, Analog Value 34
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Speed |  |  | Device 415033, Analog Output 2
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | System Fault |  |  | Device 415033, Binary Value 39
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Call Setpoint |  | °C | Device 415033, Analog Value 36
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Current Supply Temp |  | °C | Device 415032, Analog Input 0
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Primary Return Temperature |  | °C | Device 415033, Analog Input 0
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Primary Return Temperature SP |  | °C | Device 415033, Analog Value 23
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Kp |  |  | Device 415033, Analog Value 24
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Ki |  |  | Device 415033, Analog Value 25
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Min Speed |  | % | Device 415033, Analog Value 26
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Max Speed |  | % | Device 415033, Analog Value 27
TSCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Speed (ctrl) |  | % | Device 415033, Analog Output 2
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Call |  |  | Device 415033, Binary Output 1
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Status |  |  | Device 415033, Binary Value 36
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Fault |  |  | Device 415033, Binary Value 37
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Mismatch |  |  | Device 415033, Binary Value 21
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Runtime |  |  | Device 415033, Analog Value 35
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Speed |  | % | Device 415033, Analog Output 3
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | System Fault |  |  | Device 415033, Binary Value 40
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Duty Pump |  |  | Device 415033, Analog Value 39
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Manual Change Over |  |  | Device 415033, Binary Value 43
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Primary System Field DP |  | KPa | Device 415033, Analog Input 2
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Primary System Field DP SP |  | KPa | Device 415033, Analog Value 40
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Kp |  |  | Device 415033, Analog Value 41
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Ki |  |  | Device 415033, Analog Value 42
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Min Speed |  | % | Device 415033, Analog Value 43
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Max Speed |  | % | Device 415033, Analog Value 44
TPCWP-1 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Speed (ctrl) |  | % | Device 415033, Analog Output 3
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Call |  |  | Device 415033, Binary Output 1
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Status |  |  | Device 415033, Binary Value 36
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Fault |  |  | Device 415033, Binary Value 37
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Mismatch |  |  | Device 415033, Binary Value 21
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Runtime |  |  | Device 415033, Analog Value 35
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Speed |  | % | Device 415033, Analog Output 3
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | System Fault |  |  | Device 415033, Binary Value 40
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Duty Pump |  |  | Device 415033, Analog Value 39
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Manual Change Over |  |  | Device 415033, Binary Value 43
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Primary System Field DP |  | KPa | Device 415033, Analog Input 2
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Primary System Field DP SP |  | KPa | Device 415033, Analog Value 40
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Kp |  |  | Device 415033, Analog Value 41
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Ki |  |  | Device 415033, Analog Value 42
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Min Speed |  | % | Device 415033, Analog Value 43
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Max Speed |  | % | Device 415033, Analog Value 44
TPCWP-2 | Level 15 | Plantroom | Tenant Condenser Water | 415033 | Pump Speed (ctrl) |  | % | Device 415033, Analog Output 3
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | VSD Status |  |  | Device 415035, Binary Value 0
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Direction |  |  | Device 415035, Binary Value 1
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Fault Status |  |  | Device 415035, Binary Value 2
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Warning Status |  |  | Device 415035, Binary Value 3
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Hand/Auto Control |  |  | Device 415035, Binary Value 4
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Frequency |  | Hz | Device 415035, Analog Value 0
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Motor Speed |  | RPM | Device 415035, Analog Value 1
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Voltage |  | V | Device 415035, Analog Value 2
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Current |  | A | Device 415035, Analog Value 3
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Torque |  | Nm | Device 415035, Analog Value 4
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Power |  | kW | Device 415035, Analog Value 5
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Motor Temp |  | °C | Device 415035, Analog Value 6
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Kwh |  | kWh | Device 415035, Analog Value 7
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Run Time |  | h | Device 415035, Analog Value 8
Boiler-3 VSD | Roof | Plantroom | Variable Speed Drive | 415035 | Fault Reset |  |  | Device 415035, Binary Output 0
SAF-B-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Time Schedule |  |  | Device 100004, Binary Value 40
SAF-B-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Call |  |  | Device 100004, Binary Output 0
SAF-B-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Status |  |  | Device 100004, Binary Value 34
SAF-B-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Fault |  |  | Device 100004, Binary Value 35
SAF-B-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Mismatch |  |  | Device 100004, Binary Value 20
SAF-B-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Runtime |  | hrs | Device 100004, Analog Value 34
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Time Schedule |  |  | Device 100004, Binary Value 40
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Call |  |  | Device 100004, Binary Output 0
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Status |  |  | Device 100004, Binary Value 34
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Fault |  |  | Device 100004, Binary Value 35
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Mismatch |  |  | Device 100004, Binary Value 20
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Runtime |  | hrs | Device 100004, Analog Value 34
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Fan Speed |  | % | Device 100004, Analog Output 2
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Min Speed |  | % | Device 100004, Analog Value 26
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Kp |  |  | Device 100004, Analog Value 24
SAF-B-2 | Level B1 | Plantroom | Supply Air Fan | 100004 | Ki |  |  | Device 100004, Analog Value 25
SAF-B-3 | Level B1 | Plantroom | Supply Air Fan | 100004 | Time Schedule |  |  | Device 100004, Binary Value 40
SAF-B-3 | Level B1 | Plantroom | Supply Air Fan | 100004 | Call |  |  | Device 100004, Binary Output 0
SAF-B-3 | Level B1 | Plantroom | Supply Air Fan | 100004 | Status |  |  | Device 100004, Binary Value 34
SAF-B-3 | Level B1 | Plantroom | Supply Air Fan | 100004 | Fault |  |  | Device 100004, Binary Value 35
SAF-B-3 | Level B1 | Plantroom | Supply Air Fan | 100004 | Mismatch |  |  | Device 100004, Binary Value 20
SAF-B-3 | Level B1 | Plantroom | Supply Air Fan | 100004 | Runtime |  | hrs | Device 100004, Analog Value 34
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Time Schedule |  |  | Device 100004, Binary Value 40
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Call |  |  | Device 100004, Binary Output 0
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Status |  |  | Device 100004, Binary Value 34
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Fault |  |  | Device 100004, Binary Value 35
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Mismatch |  |  | Device 100004, Binary Value 20
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Runtime |  | hrs | Device 100004, Analog Value 34
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Fan Speed |  | % | Device 100004, Analog Output 2
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Min Speed |  | % | Device 100004, Analog Value 26
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Kp |  |  | Device 100004, Analog Value 24
SAF-G-1 | Level B1 | Plantroom | Supply Air Fan | 100004 | Ki |  |  | Device 100004, Analog Value 25
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Time Schedule |  |  | Device 415031, Binary Value 40
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Call |  |  | Device 415031, Binary Output 0
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Status |  |  | Device 415031, Binary Value 34
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Fault |  |  | Device 415031, Binary Value 35
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Mismatch |  |  | Device 415031, Binary Value 20
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Runtime |  | hrs | Device 415031, Analog Value 34
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | CO Level |  | ppm | Device 415031, Analog Input 0
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | CO Setpoint |  | ppm | Device 415031, Analog Value 23
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Fan Speed |  | % | Device 415031, Analog Output 2
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Kp |  |  | Device 415031, Analog Value 24
CPEF | Level B1 | Plantroom | Car Park Ventilation | 415031 | Ki |  |  | Device 415031, Analog Value 25
TEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Call |  |  | Device 415031, Binary Output 0
TEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Status |  |  | Device 415031, Binary Value 34
TEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Fault |  |  | Device 415031, Binary Value 35
TEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Mismatch |  |  | Device 415031, Binary Value 20
TEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Runtime |  | hrs | Device 415031, Analog Value 34
TEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Time Schedule |  |  | Device 415031, Binary Value 40
TEF-15-2 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Call |  |  | Device 415031, Binary Output 0
TEF-15-2 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Status |  |  | Device 415031, Binary Value 34
TEF-15-2 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Fault |  |  | Device 415031, Binary Value 35
TEF-15-2 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Mismatch |  |  | Device 415031, Binary Value 20
TEF-15-2 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Runtime |  | hrs | Device 415031, Analog Value 34
TEF-15-2 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Time Schedule |  |  | Device 415031, Binary Value 40
GREF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Call |  |  | Device 415031, Binary Output 0
GREF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Status |  |  | Device 415031, Binary Value 34
GREF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Fault |  |  | Device 415031, Binary Value 35
GREF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Mismatch |  |  | Device 415031, Binary Value 20
GREF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Runtime |  | hrs | Device 415031, Analog Value 34
GREF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415031 | Time Schedule |  |  | Device 415031, Binary Value 40
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Any AHU Status |  |  | Device 415033, Binary Value 44
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Call |  |  | Device 415033, Binary Output 0
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Status |  |  | Device 415033, Binary Value 34
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Mismatch Fault |  |  | Device 415033, Binary Value 20
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Runtime |  | hrs | Device 415033, Analog Value 34
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Static Pressure |  | Pa | Device 415033, Analog Input 0
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Static Pressure SP |  | Pa | Device 415033, Analog Value 23
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Kp |  |  | Device 415033, Analog Value 24
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Ki |  |  | Device 415033, Analog Value 25
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Minimum Speed |  |  | Device 415033, Analog Value 26
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Fan Speed |  | % | Device 415033, Analog Output 2
TGEF-15-1 | Level 15 | Plantroom | Exhaust Air Fans | 415033 | Fault |  |  | Device 415033, Binary Value 35
KEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Time Schedule |  |  | Device 415031, Binary Value 40
KEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Call |  |  | Device 415031, Binary Output 0
KEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Status |  |  | Device 415031, Binary Value 34
KEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Fault |  |  | Device 415031, Binary Value 35
KEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Mismatch |  |  | Device 415031, Binary Value 20
KEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Runtime |  | hrs | Device 415031, Analog Value 34
KEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Fan Speed |  | % | Device 415031, Analog Output 2
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Call |  |  | Device 415031, Binary Output 0
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Status |  |  | Device 415031, Binary Value 34
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Fault |  |  | Device 415031, Binary Value 35
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Mismatch |  |  | Device 415031, Binary Value 20
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Runtime |  | hrs | Device 415031, Analog Value 34
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Time Schedule |  |  | Device 415031, Binary Value 40
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Fan Speed |  | % | Device 415031, Analog Output 2
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Static Pressure |  | Pa | Device 415031, Analog Input 0
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Static Pressure SP |  | Pa | Device 415031, Analog Value 23
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Kp |  |  | Device 415031, Analog Value 24
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Ki |  |  | Device 415031, Analog Value 25
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Min Speed |  | % | Device 415031, Analog Value 26
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Max Speed |  | % | Device 415031, Analog Value 27
SEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | System Fault |  |  | Device 415031, Binary Value 39
TEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Time Schedule |  |  | Device 415031, Binary Value 40
TEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Call |  |  | Device 415031, Binary Output 0
TEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Status |  |  | Device 415031, Binary Value 34
TEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Fault |  |  | Device 415031, Binary Value 35
TEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Mismatch |  |  | Device 415031, Binary Value 20
TEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Runtime |  | hrs | Device 415031, Analog Value 34
TEF-16-1 | Roof | Plantroom | Exhaust Air Fans | 415031 | Fan Speed |  | % | Device 415031, Analog Output 2
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | VSD Status |  |  | Device 205004, Binary Value 0
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Direction |  |  | Device 205004, Binary Value 1
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Fault Status |  |  | Device 205004, Binary Value 2
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Warning Status |  |  | Device 205004, Binary Value 3
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Hand/Auto Control |  |  | Device 205004, Binary Value 4
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Frequency |  | Hz | Device 205004, Analog Value 0
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Motor Speed |  | RPM | Device 205004, Analog Value 1
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Voltage |  | V | Device 205004, Analog Value 2
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Current |  | A | Device 205004, Analog Value 3
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Torque |  | Nm | Device 205004, Analog Value 4
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Power |  | kW | Device 205004, Analog Value 5
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Motor Temp |  | °C | Device 205004, Analog Value 6
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Kwh |  | kWh | Device 205004, Analog Value 7
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Run Time |  | h | Device 205004, Analog Value 8
OAF-G-01 | Ground | Plantroom | Exhaust Air Fans | 205004 | Fault Reset |  |  | Device 205004, Binary Output 0
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | VSD Status |  |  | Device 205004, Binary Value 0
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Direction |  |  | Device 205004, Binary Value 1
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Fault Status |  |  | Device 205004, Binary Value 2
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Warning Status |  |  | Device 205004, Binary Value 3
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Hand/Auto Control |  |  | Device 205004, Binary Value 4
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Frequency |  | Hz | Device 205004, Analog Value 0
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Motor Speed |  | RPM | Device 205004, Analog Value 1
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Voltage |  | V | Device 205004, Analog Value 2
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Current |  | A | Device 205004, Analog Value 3
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Torque |  | Nm | Device 205004, Analog Value 4
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Power |  | kW | Device 205004, Analog Value 5
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Motor Temp |  | °C | Device 205004, Analog Value 6
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Kwh |  | kWh | Device 205004, Analog Value 7
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Run Time |  | h | Device 205004, Analog Value 8
GEF-L05-01 | Level 5 | Plantroom | Exhaust Air Fans | 205004 | Fault Reset |  |  | Device 205004, Binary Output 0
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | VSD Status |  |  | Device 205004, Binary Value 0
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Direction |  |  | Device 205004, Binary Value 1
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Fault Status |  |  | Device 205004, Binary Value 2
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Warning Status |  |  | Device 205004, Binary Value 3
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Hand/Auto Control |  |  | Device 205004, Binary Value 4
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Frequency |  | Hz | Device 205004, Analog Value 0
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Motor Speed |  | RPM | Device 205004, Analog Value 1
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Voltage |  | V | Device 205004, Analog Value 2
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Current |  | A | Device 205004, Analog Value 3
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Torque |  | Nm | Device 205004, Analog Value 4
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Power |  | kW | Device 205004, Analog Value 5
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Motor Temp |  | °C | Device 205004, Analog Value 6
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Kwh |  | kWh | Device 205004, Analog Value 7
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Run Time |  | h | Device 205004, Analog Value 8
OAF-L05-01 | Level 5 | Plantroom | Supply Air Fan | 205004 | Fault Reset |  |  | Device 205004, Binary Output 0

## equipment_types
equipment_types
Active Chilled Beams
Air Cooled Condensers
Air Curtain
Air Handling Units
Air to Air Heat Exchanger
BACER
Bacer (System)
Bathroom Fixtures
Boiler
Buffer Tank
Building
Calorifier
Car Park Ventilation
Car Plug
Chiller
Chiller Plant
Cold Water Booster Pumps
Combined Heating & Power
Compressed Air
Computer Room Air Conditioning Unit
Condenser Water Pumps
Cooling Tower
Domestic Cold Water
Domestic Hot Water
Dry Cooler
Econet Heat Recovery Unit
Elevator
Exhaust Air Fans
Fan Coil Units (Legacy)
Fire Integration Panel
Gas Detector
Gas Meters
Gas Meters (System)
Gas Turbines
Generator
Heat Exchanger
Heat Pump
Heat Recovery Unit
Hydraulic Pump
Kitchen Fans - See Exhaust or Supply Fan
Light
Miscellaneous Pump
Natural Ventilation
Packaged Air Conditioning Units
Passive Chilled Beams
People
Power Meters (System)
Power Sub-Meters
Primary Chilled Water Pumps
Primary Hot Water Pumps
Rain Water Tank
Refrigeration
Secondary Chilled Water System
Secondary Hot Water System
Solar Water Heater
Steam Boiler
Steam Meter
Steam Trap
Supply Air Fan
Tenant Condenser Water
Thermal Energy Meters
Thermal Labyrinth
Thermostat
Unassigned
Under-Floor Heating System
Uninterruptible Power Supply
Unit Heater
Variable Air Volume
Variable Refrigerant Volume Systems
Variable Speed Drive
Vertical Transport
Water Leak
Water Meters
Water Meters (System)
Water Treatment
Weather (System)
Zones